FLOOD EMERGENCY RESPONSE PLAN

Note: No one flood emergency response plan (FERP) can be designed to address all conditions. Use this document as a basic guide in developing your own FERP. Items that do not apply can be omitted; other items can be expanded, or added, as appropriate.

Revision Date:

Company Name:

Location Name:

Address, City, State:

Index-Record Number:

Account Number:

# table of contents

A.	Purpose

B.	Site Flood Hazard

C.	Authority to Activate Plan

D.	Flood Monitoring

E.	Flood Action Plan

Facility Shutdown

Flood Mitigation

F.	Fire Hazard Mitigation

G.	Recovery Plan

Fire Protection Restoration

Restoration of Operations

H.	Post-Event Review

I.	FERP Training Exercises

J.	References

K.	Attachments (as needed)

## Purpose

This FERP is an outline of actions to be taken before, during and after a flood. With proper planning, both property damage and business interruption can be minimized. The plan should be reviewed and updated annually to make sure effective action is taken, as needed. Preparation considers the depth of flooding based on predictive probabilities of up to the Moderate Hazard, 0.2% annual chance flood event.

## Site Flood Hazard

Flood hazards are unique and site-specific. Understanding the potential scenarios faced by any individual site provides for the development of plan components that will be most appropriate with a higher level of success. Consult your local FM Global engineer or flood specialist for assistance in developing the overall Site Flood Hazard.

Provide a high-level description of the flood hazard(s) and likely scenario(s) including the following:

Source(s) of flooding

Likely weather event(s) that will trigger flood

Likely advanced warning time for each event

Depth of water if expected to affect site ingress and egress

Depth of water expected in key buildings

Length of time water will remain in the facility for each event

Description of critical areas likely to be flooded

Anticipated business impact

Describe the areas potentially affected and where the site is vulnerable to water entry. Each potential entry point should be listed (including any pertinent photos or maps) in order of priority where water will most likely enter first. This will serve as a lead-in to describing the areas to monitor during any event.

Water Entry Points

| Building/Area | Opening and Elevation | Notes |
| --- | --- | --- |

## Authority to Activate Plan

The authority to activate the plan is critical, as business operations may be temporarily halted and access restricted to reduce the overall damage and potential business interruption.

Describe who has the ultimate authority to activate response actions. Ensure an authorized person, such as a plant or operations manager, is responsible for each shift, and identify an alternate individual, as needed.

| Authority to Activate Plan | Main Phone | Alternate Phone |
| --- | --- | --- |

Additional Contacts

| Plant Contacts | Main Phone | Alternate Phone |
| --- | --- | --- |
| Emergency Plan Coordinator |  |  |
| General Manager |  |  |
| Maintenance Manager |  |  |
| Security |  |  |

| Local Authorities | Phone Number | Website/Email |
| --- | --- | --- |
| Police Department |  |  |
| Fire Department |  |  |
| Local Emergency Management Agency |  |  |
| National Weather Service Office |  |  |

| Key Vendors | Phone Number | Website/Email |
| --- | --- | --- |

## Flood Monitoring

The plan should indicate when monitoring operations are to begin, the preferred method of monitoring, and who has the responsibility for this critical step. A person or position, with alternates, should be assigned to monitor local conditions on each shift.

| Shift | Person/Position to Monitor | Alternate |
| --- | --- | --- |

Possible methods to monitor weather conditions leading to potential flood events include:

The National Weather Service

Special weather bulletins

Local emergency management agency

Local TV stations

Local TV station websites for weather radar

On-site closed-circuit cameras focused on vulnerable points

Possible methods to monitor site-specific water levels, rate-of-rise and projections include:

If river – official river gauge forecasting sources (U.S. – Advance Hydrologic Prediction Service)

If creek/stream/ditch – local gauge, low breach points, observed water elevation to impact levels

If bridges or culverts, monitor for obstructions leading to impoundment or diversion

Low site drains in yard, dock areas, pits, basements, or sumps

High-water alarms in low-level sumps, pits, etc.

Consider installation of a localized water level gauge to monitor on or near site conditions

Specific water levels or precautionary predictions should be designated to trigger the action steps listed in the Flood Action Plan below. The trigger point should be based on the amount of time needed to accomplish the response action steps and the amount of advance warning time available. See 
FM Global Property Loss Prevention Data Sheet 1-40 Flood, sections 3.3, Strategy to Understanding 
the Flood Potential and 3.4, Understanding Flood Sources and Their Characteristics for guidance with advanced warning.

## Flood Action Plan

This section must be completed by facility personnel. Items that should be considered and included are listed below. Specific action steps with the flood levels/predictions/local observations that trigger each step should be established and documented, along with required manpower and equipment for completion. This activity will help prioritize the tasks, which may be very important, if time is limited.

If the FERP includes deployment of flood protection equipment (barriers, gates/doors, sump pumps, etc.) and controlled shutdown of critical equipment, ensure each task necessary to implement the plan is documented and flood responders are assigned for all shifts.

### Facility Shutdown

Procedure to shut down/de-energize utilities in an orderly manner to reduce ignition sources and damage:

- Plan for a safe emergency shutdown of operations.

- Plan for shutdown of utilities (electric, fuel, etc.).

- Shut down ignitable liquid and flammable gas systems.

| Building/ Equipment | Shutdown Activity | Time Needed | Assigned To | Water or Gauge Level to Begin Action |
| --- | --- | --- | --- | --- |

### Flood Mitigation

Action items are best prioritized considering the value of the mitigation action combined with achievability within the advance warning window available. Some typical examples not in any type of prioritized order, 
are provided below:

- Control ignition sources.

- Stop all incoming shipments and expedite outgoing shipments.

- Raise and relocate highly valuable and easily moved equipment, contents and vital records to higher elevations. This may necessitate acquiring or renting special equipment to relocate contents. Rank level of importance.

- Close emergency valves to sewer drains.

- Check sump pumps to ensure they are operable.

- Deploy flood defense equipment such as barriers, doors and floodgates.

- Ensure backup power supplies (generators) are functional.

- Apply water-displacing, rust-preventive compound to equipment that may become partially or fully submerged.

- Fill empty storage tanks to prevent them from floating.

- Relocate/reroute supplies.

- Relocate/elevate critical files, stock, portable high-value equipment, etc.

- Set up emergency communication apparatus.

- Deploy site security. Monitor access to property and outside utilities during flooding.

- Begin communication to obtain portable temporary electrical devices, fans, dehumidifiers, etc., 
needed for salvage operations.

| Building/ Equipment | Shutdown Activity | Time Needed | Assigned To | Water or Gauge Level to Begin Action |
| --- | --- | --- | --- | --- |

## Fire Hazard Mitigation

- Eliminate all unnecessary open flames or heat sources, including smoking.

- Keep fire protection equipment operational for as long as possible. Use the FM Global Red Tag Permit System to document any fire protection equipment shutdown.

- Perform hot work only if there are no safer alternatives. Use the FM Global Hot Work Permit System to supervise any work being performed on the property. Hot work should only be performed after fire protection systems are restored and combustibles are removed from the hot work area.

- Provide necessary electrical services, with restoration on an item-by-item basis, only after a thorough check by competent qualified personnel.

- Check all ignitable liquid storage and flammable gas piping systems for leaks before returning to operation.

- Check all tanks for leaks.

- Establish a procedure to remove all combustible debris as it accumulates.

- Initiate a continual fire watch until normal operations are resumed.

## Recovery Plan

This section must be completed by facility personnel. Contact critical contractors and suppliers in advance of the salvage operations, to ensure they will be available when needed. Initial efforts should focus on preventing further loss from complications of the flood. Once the site is secure, efforts should be focused on restoring the facility operations.

### Fire Protection Restoration

Promptly return fire protection systems to service by taking the following actions:

- Run or test fire pump, fire pump driver, and controller. Repair if flood-damaged.

- Examine the fire pump water source (particularly for open bodies of water) to ensure debris will not enter the pump suction line and sprinkler system.

- Check the yard main fire protection system and water tanks for washouts.

- Remove water and mud from fire protection valve pits.

- Inspect sprinkler system piping for damage, and repair as needed.

- Test all sprinkler control valves to ensure they are fully open, operable and undamaged.

- Check all fire protection alarm systems and make necessary repairs.

| Building | Fire Protection Equipment |
| --- | --- |

### Restoration of Operations

- Prioritize cleanup actions.

- Prioritize the rebuilding or replacement of pieces of equipment that are most critical.

- Contingency planning for prolonged site isolation:

- Relocate operations.

- Set up temporary or skeleton operation at remote locations.

- Document procedures on how production will be made up at other facilities.

- Establish agreements with vital subcontractors to respond in the event of flooding.

- Initiate salvage and cleanup operations by a designated salvage crew. Focus efforts on:

- Removing excess water, submerged carpet and wet equipment and contents, and washing down any mud or silt accumulations.

- Providing of high-volume fans and dehumidifiers to begin the drying process.

- Removing wallboard, or providing access panels to facilitate air movement within gypsum board, plaster or wooden walls.

- Initiating drying, cleaning and application of rust-preventive coatings to mechanical and electrical equipment.

- Relocating salvageable and undamaged stock and supplies to a safe area.

| Building/Equipment | Restoration Activity |
| --- | --- |

## Post-Event Review

Review the plan after each flooding to identify areas for improvement, and to determine if any changes need to be made to the site and facility to reduce the magnitude of emergency actions.

## FERP Training Exercises

Conduct regular FERP training exercises that involve all staff required to respond; and at least once a year, organize a complete dry run to simulate the flood event.

## References

FM Global Property Loss Prevention Data Sheets

Data Sheet 10-1, Pre-Incident and Emergency Response Planning

Data Sheet 1-40, Flood

FM Approvals – Approval Guide

## Attachments (as needed)

- Facility maps

- Flood maps

- Fire protection valve list

- Fire protection contractor(s)

- Insurance carrier contact details

- List of equipment suppliers

- List of restoration and cleaning contractors

# Appendix – Annual Review

Review the plan annually to confirm validity of its contents and the familiarity of personnel relied upon for its execution. Plan content may also be updated as facility changes occur.

- List of personnel involved with training and review of plan.

- Date of annual review session.